## Section 1
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 1 -Preliminaries and General requirements
Item | Description | Unit | Estimated Quantity | Unit rate | Amount
|  |  |  | (USD) | (USD)
1.1 | Mobilization and Demobilization | LS | 1 |  | 0
1.2 | Complementary design documents, construction documents, shop drawings, as-built drawings and Operation and Maintenance manuals | LS | 1 |  | 0
1.3 | Provisional sum | PS | 1 | 20000 | 20000
SUMMARY |  | 20000

## Section 3
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 3 -Concrete works
Item | Description | Unit | Estimated Quantity | Unit rate | Amount
|  |  |  | (USD) | (USD)
3.1 | Cast-in-place plain concrete Cast-in-place plain concrete, complete including all necessary formwork and accessories, all as specified, shown on the drawings, in the specifications and to the satisfaction of the Supervisor.
3.1.1 | Cast-in-place plain concrete, Cement Type II, 14 MPa, for blinding for foundation (various structures and buildings) Cast-in-place plain concrete using Moderately Sulphate Resistant Cement to ASTM C150, Type II, 14 MPa on cylinder, for blinding for foundation beds (100 mm thick), complete including all necessary formwork and accessories, all as specified, shown on the drawings and to the satisfaction of the Supervisor. | m3
3.1 | Cast-in-place concrete Cast-in-place concrete for concrete using High Sulphate Resistant Cement to ASTM C150, Type V, 30 MPa on cylinder, complete including formwork of any type and any shape, accessories, construction joints, waterstops to each casting edge, inserts for openings, sleeves, etc., and all other related works, all as specified, shown on execution drawings and to the satisfaction of the Engineer (for the closure of the composting hangar) | m3 | 40 |  | 0 | 28.44 | 15.64
3.2 | Steel reinforcement bars for reinforced concrete work, yield stress 420 N/mm2 high tensile steel grade 60 (for the closure of the partially open sorting hangar, and the closure of the composting hangar) | Kg | 4400 |  | 0
3.3 | Steel reinforcement bars for stirrups and hoops for reinforced concrete work, grade 40 (for the closure of the partially open sorting hangar, and the closure of the composting hangar) | Kg | 440 |  | 0
SUMMARY |  | 0

## Section 6
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 6 -Blockworks
Item | Description | Unit | Estimated Quantity | Unit rate | Amount
|  |  |  | (USD) | (USD)
6.1 | Non-load-bearing hollow blockwork (OPC)
6.1.1 | Non-load-bearing hollow Blockwork 20 cm thick (OPC) (for the the closure of the composting hangar) | m2 | 550 |  | 0
6.2 | Removal of the existing stone/blockwork border laid at ground level of the composting hangar | LS | 1 |  | 0
SUMMARY |  | 0

## Section 7
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 7-Joinery and Ironmengary
Item | Description | Unit | Estimated Quantity | Unit rate | Amount
|  |  |  | (USD) | (USD)
7.1 | Closure of the composting hangar open accessways by the means of a manually operated two-leaves painted metallic sliding door of dimensions, height 5.4m x width 4.5m composed of two 1.2mm corrugated steel panels sandwiched by metal reinforcement, as stated in the specifications, shown on the drawings, or directed by the Engineer. | Unit | 2 |  | 0
SUMMARY |  | 0

## Section 9
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 9-Floor, walls, ceilings and finishes
Item | Description | Unit | Estimated Quantity | Unit rate | Amount
|  |  |  | (USD) | (USD)
9.1 | Render
9.1.1 | Interior rendering (cement type I - OPC) | m2 | 550 |  | 0
SUMMARY |  | 0

## Section 19
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SECTION 19-Miscellaneous works
Note:
The price includes the complete execution of the Biofilter odour control system according to the requirements of the Tender Documents, notably the Particular Technical Specifications and the Bill of Quantities.
- Preparation of detailed execution drawings and shop drawings
- Site preparation
- Supply, transportation and installation of biofilter equipment with all associated units and accessories (including axial fans extracting air from the sorting hangar and injecting it into the composting hangar, centrifugal fans extracting fouled air from the composting hangar to the odor control unit, an extraction and collection duct system spanning the periphery of the composting hangar till the odor control unit prescrubber system, a chemical dosing station, water tank and distribution pipes, miscellaneous piping, water supply networks, equipment and accessories, drainage networks, manholes, equipment and accessories, humidity sensors, pumps, etc. as specified elsewhere in these Tender Documents)
- Supply, transportation and installation of Biofilter media
- Fumigation for the biofilter media before transport to Lebanon and the project area including addition of 0.7 Kg/m3 of urea (at 46%), as well as composting, overcasting and post-fermentation of the material for 4-5 weeks
- All associated civil works including excavations and earthworks (including the execution of the elevated platform below the Biofilter odour control system), iincluding, among others, site clearance and excavation, filling and backfilling, sub-base course layers and base course layers, damp proof membrane,), blinding concrete, foundations, reinforced concrete works, manholes, surface coating and protection, etc., complete for the complete execution of the biofilter system
- All associated electrical works including power supply, electrical panels, cables, cable protection, earthing, necessary for the execution and operation of the biofilter odor treatment system and its various associated equipment and accessories till the connection of the complete biofilter system to the main control panel, etc.
- All necessary accessories
- Testing and commissioning
- All other related works, all as specified, and to the satisfaction of the Engineer
The price for this item, completely executed and tested, shall be paid as a lump sum.
Note: the works related to the various execution of the elevated platform (to prevent flooding) is included within the price of the Biofilter odour control system
Description | Unit | Estimated quantity | Unit rate | Amount
|  |  | (USD) | (USD)
Construction, installation, testing and commissioning of the complete biofilter system including the various components described herebelow as well as in the various sections of these Tender Documents (and mainly the Particular Technical Specifications): | LS | 1 |  | 0
SUMMARY | 0
Construction, installation, testing and commissioning of the biofilter unit provided with the following characteristics:
Capacity 40,000 m3/h
Inside dimensions of the biofilter:
- Length: 26.0 m
- Width: 10.0 m
- Height of biofilter walls: 2.2m
- Height of media: 1.6m divided as such:
Type of media:
- A distribution layer composed of pre-fermented root wood (broken and fibrous root timber mainly from root stocks), of height around 0.4m, composed of pine wood (in a proportion of around 85%), and foliage tress (in a proportion of around 15%)
- A main layer composed of pre-fermented pine bark with wooden pieces pine bark, of height around 1.2m, composed of pine bark (in a proportion of around 60%) originating from fresh untreated materials from saw mill, and wood partly sticking to the bark (in a proportion of around 40%). The material should offer low pressure drop, efficient and constant pollution degradation of fouled air quality, and a capacity to accommodate for fluctuations in humidity. Pine bark with wood fraction acts as an efficient buffer, keeping an optimal pH in the filter medium. Without slacking a constant streaming (without channeling) shall be provided.
Under optimum conditions, operating times and lifetime of the media shall be between 3 and 6 years, with a minimum required of at least 4 years, without any material change
Ancillary items to be executed:
- Execution of a drainage pit at the bottom of the biofilter bed to convey the percolated liquid out of the biofilter and towards a collection manhole/sump pit to be executed near the biofilter and equipped with a submersible pump, with piping and accessories to allow the pumping of the drained liquid towards the leachate collection tank; as described elsewhere in these Tender Documents and notably in the Particular Technical Specifications and the Preamble to Bill of Quantities
- Execution of a bed access opening in the body of the biofilter structure to allow filling and inspection of the media bed. It shall be closed by timber planks in steel profile and can be chosen according to local requirements by the Contractor and approved by the Engineer.
The system also includes:
- PVC Plastic support plates/grids, height 0.6m
- Prescrubber unit
Construction, installation, testing and commissioning of the prescrubber unit provided with the following characteristics:
Capacity: 40,000 m³/h
Inside dimensions of the prescrubber unit:
Length: 1.6 m
Width: 10.1 m
Height: 2.2 m
Including also:
- Packing material made of polypropylene with a specific surface area between 90-100 m2/m3 and a free volume between 90 and 100%.
- Droplet separator
- Recirculation pump (2 duty and 1 backup stored in stock)
- Recirculation pipe with pressure gauge and spraying nozzles
- Measuring equipment
- Level control for the pump sump (incl. overflow and drainage)
- Dry-run protection for the pump
- All internal piping
- Dosing station
Construction, installation, testing and commissioning of the prescrubber dosing station realizing dosing of acid (H2SO4 < 76%).
Including a dosing pump built in pre-scrubber housing, Suction and dosing line (10 m each), pH probe, Measuring and control devices, chemicals storage tank. 1 additional backup dosing pump is to be provided in stock.
Construction, installation, testing and commissioning of the biofilter odor control system centrifugal fan:
This item shall include but not be limited to:
Procuring, transporting, storing, installing, painting, remedying of all defects that may appear while testing of centrifugal inline fans and all other accessories necessary for the proper execution of this item as shown on the drawings, required by the specifications and / or deemed necessary by the Engineer.
- Number of fans: 2 (1 duty + 1 standby)
- Unit capacity: 40,000 m³/h
- Stat. pressure: 2,000 Pa
- Motor: 37 kW, suitable for VFD operation
Materials
- Impeller: Alue 231
- Housing: Stainless Steel 1.4301
- The fans shall be heavy duty resistant to corrosion
Execution of all corresponding civil works required for the construction, installation, testing and commissioning of the complete odor control biofilter system including:
- General excavation/Site preparation and clearance of a depth of 30cm, shall include removing and disposal of vegetation, undergrowth, bushes, hedges, trees, debris, trash and the like, disconnecting and sealing services (as applicable) and excavation of the top superficial soil layer to eliminate the organic or inadequate top soil. Site preparation and clearance shall be carried out to the satisfaction of the Engineer to enable and facilitate all new construction
- Eventual soil replacement of unsuitable soil material
- Grading and compaction of the natural ground level after excavation to a dry density not less than 95% of the Optimum Standard Proctor dry density
- Installation of a geotextile layer (250g/m2) above the compacted natural ground level after excavation, according to the specifications herebelow
- Execution of the outer walls of the biofilter system exposed to the outside (i.e. with the exception of the side connecting to the prescrubber) by the means of:
o Cast-in-place reinforced concrete walls, using High Sulphate Resistant Cement to ASTM C150, Type V, 30 MPa tested on cylinder (38 MPa on cube).
o Provided with a protective coating on the internal surfaces (coal tar epoxy coating in 2 layers, total thickness 400 microns minimum);
- The underground part of the walls shall also be provided with a bituminous coating layers for external surface (2 layers)
- The wall footings shall also be provided with:
o A bituminous coating layers for external surface (2 layers)
o A 10cm layer of blinding concrete under the wall footings, cast-in-place plain using ordinary Portland cement to ASTM C150, Type I, 16 MPa on cylinder.
- Execution of the wall footings on the following two layers (from top to bottom):
o A 40cm thick minimum well graded base course layer (CBR 70%),
o A 60cm thick minimum well graded subbase course layer (CBR 50%),
- Execution of the bottom slab of the complete biofilter system (i.e. biofilter, under prescrubber and under centrifugal fans) by the means of the following (from top to bottom):
o Cast-in-place reinforced concrete walls, using High Sulphate Resistant Cement to ASTM C150, Type V, 30 MPa on cylinder.
o Provided with a protective coating on the internal surfaces (coal tar epoxy coating in 2 layers, total thickness 400 microns minimum);
o A damp proof membrane above the base course layer
- Execution of the bottom slab on the following two layers (from top to bottom):
o A 40cm thick minimum well graded base course layer (CBR 70%),
o A 30cm thick minimum well graded subbase course layer (CBR 50%),
Construction, installation, testing and commissioning of the sorting hangar air extraction axial fan to push air from the sorting hangar to the composting hangar:
This item shall include but not be limited to:
Procuring, transporting, storing, installing, painting, remedying of all defects that may appear while testing of propeller fans and all other accessories necessary for the proper execution of this item as shown on the drawings, required by the specifications and / or deemed necessary by the Engineer.
- Number of fans: 3 (2 duty, and 1 backup stored in stock)
- Unit capacity: 18,000 m³/h
- Stat. pressure: 600 Pa
- Motor: 7.5 kW
Materials
- Impeller: Alue 231
- Housing: Stainless Steel 1.4301
- The fans shall be heavy duty resistant to corrosion
Execution of galvanized steel ducts with support fixtures on the metal structures, to be installed along the composting hangars to allow fouled air extraction from various locations within the hangar till the odor control treatment system.
This item shall include but not be limited to:
Procuring, transporting, storing, installing, painting, remedying of all defects that may appear while testing of supply, return and ventilation galvanized metal sheet rectangular / Circular air ducts, including seams, joints, reinforcements, hangers, supports, splitter, turning vanes, elbows and transformation complete with duct sealants and flexible connections and Plenum box with 15mm internal liner glued and fixed with pins to the duct complete with external fiber glass insulation as specified and described herein, with galvanized steel corners on the edges and all necessary accessories complete with round Volume damper on each inlet (where shown on the drawings) and all other accessories necessary for the proper execution of this item as shown on the drawings, required by the specifications and / or deemed necessary by the Engineer.
Duct construction to be done according to specifications as "SMACNA" duct construction standards
Execution of all corresponding electrical works required for the construction, installation, testing and commissioning of the complete biofilter system and air extraction systems including:
Execution of local control panels for the biofilter system as well as for the axial extraction fans. The control panel shall be conveniently located to give fingertip management of all machine functions. All associated electrical works including power supply, electrical panels, cables, cable protection, earthing, necessary for the execution and operation of the biofilter odor treatment system and its various associated equipment and accessories shall be executed including:
- The works necessary for the connection of the biofilter system to the local control panel to be installed
- The works necessary for the connection of the axial fans extraction system to the local control panel to be installed
- The works necessary for the connection of the two aforementioned local panels to the main control panel distribution board located in the administration building. The cable section will be minimum 3x35 mm2 + 16mm2
The electrical works shall include fabrication, factory testing, supply, transportation, storage, installation, site testing, commissioning, O&M manuals, also supplying and installation of all corresponding controls, fittings, supports, accessories and civil works required to complete installation of the equipment according to the specifications and direction of the Engineer.
The contractor must submit the catalogues for all the electrical and instrumentation equipment to the approval of the Engineer before the purchase order
Execution of Ancillary works
- Equipping, followed by testing and commissioning, of the main facility water tank (connected to the public water supply grid) with pumps, pipes and accessories in order to pump water to a foreseen plastic water tank to be constructed near the biofilter system.
- Construction, installation, testing and commissioning of this foreseen plastic water tank near the biofilter system, to be executed on an elevated support to ensure gravity feeding, and the equipping of this latter tank with its piping, valves and accessories to allow gravity connection to the prescrubber sump. This item shall include but not be limited to: - Procuring, transporting, storing, installing, painting, remedying of all defects that may appear while testing of plastic water tank and all other accessories necessary for the proper execution of this item as required by the specifications and / or deemed necessary by the Engineer.

## Summary
Mercy Corps
IJMAA-Odor control system
Odor treatment system for Jebb Jennine Solid Waste Treatment Facility |  |  | Name of Bidder:
SUMMARY
SUMMARY
Description |  |  | …………………………………………………………………………………………………………………………………………………………………. |  | Amount (USD)
SECTION 1 -Preliminaries and General requirements
SECTION 3 -Concrete works |  |  |  |  | 0
SECTION 6 -Blockworks |  |  |  |  | 0
SECTION 7-Joinery and Ironmengary |  |  |  |  | 0
SECTION 9-Floor, walls, ceilings and finishes |  |  |  |  | 0
SECTION 19-Miscellaneous works |  |  |  |  | 0
| Total Amount of Bill of Quantities ………………………………………………………………………………………. |  |  |  | 0
| Discount by Tenderer ( ______ %) ………………………………………………………………………………………. | 1e-25% |  | 25%
| Total Amount of Tender after Discount ………………………………………………………………………………………. |  |  |  | 0
Total Amount of Tender after Discount in Words:
USD Only:
| VAT (11%) | 1e-25% |  | 25% | 0
| Total Amount of Tender after Discount , including VAT |  |  |  | 0
* | Total Amount of Tender after Discount , including VAT, in words :
USD Only:
* TOTAL AMOUNT AFTER DISCOUNT TO BE REGISTERED IN FORM OF BID