## BoQ 04_Ganye_GRA GGS and PS
ADAMAWA STATE
Small Towns Water Supply
| Government Primary and Secondary School Sangassumi (GANYE LGA) |  |  |  | Bill 03
Item No | Description | Unit | Unit Price (Naira) | Estimated Qty | Amount
(Naira)
Borehole Upgrading, cleaning and test-pumping
101 | Carry out borehole cleaning and development by backwashing, jetting and airlifting | Hr |  | 3 | 0
102 | Equip the borehole with suitable pumpset and ancillary equipment for a 24 pumping test to establish maximum and safe yield from the borehole. Include for measurements and records of discharge water | No |  | 1 | 0
103 | Carry out water quality analysis, including full bacteriological and physico-chemical analysis | No |  | 1 | 0
104 | Carry out disinfection of the motorised borehole, permanent pump and riser pipes as specified | No |  | 1 | 0
105 | Supply and installation of solar pump type SQ flex +CU200 Type Grundfos or equivalent type/standard) complete with cable, starter/swithces and accessories (provisional). Note: Actual parameters to be determined only from pump-testing result after drilling. | No |  | 1 | 0
106 | Supply and installation of 75 mm dia. UPVC Pipes of 10 bar flanged with all connections to form rising main | m |  | 1 | 0
107 | Supply and Install 3m scotch cast cable jointing kits and earthing | No |  | 1 | 0
108 | Supply and Installation of Solar Mono polycrystalline panels as in TSS | Watts |  | 1 | 0
109 | Supply and Install support structure and frames for panels | No |  | 1 | 0
110 | Supply and Install 3x6mm2 pump motor cable | Set |  | 1 | 0
111 | Supply and Install 4mm2 interconnector cable | Set |  | 1 | 0
112 | Supply and install Marine rope 10mm as antidrop for the pump | Roll |  | 1 | 0
113 | Provide and install header pipework, in 75mm dia upvc pipes, fittings, and appurtenances including 1 no 90 deg and 2 nos 45 deg bends, air valve, gate valve, non-return valve, pressure gauge and flow meter. | No |  | 1 | 0
114 | Carry out 6-hour pump test after installation of permanent pump | Hr |  | 6 | 0
115 | Prepare Technical Report (allow 5 copies) for the borehole test pumping and construction details. Include for borehole material logs, yields, recovery, water quality analysis (full chemical and bacteriological) and borehole vertical alignment. | Ls |  | 1 | 0
0
116 | Carry out down-the-hole camera inspection to confirm construction and structural integrity of borehole | No |  | 1 | 0
117 | Carry out borehole cleaning and development by backwashing, jetting and airlifting | Hr |  | 3 | 0
Sub-Total Page to Borehole Works Summary |  |  |  |  | 0
COLLECTION SHEET
Summary Borehole Works
| Sheet 2 |  |  |  | 0
Total Borehole Works |  |  |  |  | 0
Treatment Plant
200 | Treatment is required for pH correction and disinfection only.
Dosing Pumps
201 | Chemical dosing set for each of Soda ash(Sodium Carbonate) and Chlorine (Calcium hypochlorite), including Dosing Pump with pumping rate 50 Litres/Hr and 4 bar working pressure, mixing tank 1000 Litres, level indicator and chemical agitator, 12mm dia uPVC connection pipework and all ancillaries for complete system installation. | LS |  | 1 | 0
0
| Storage Tanks |  |  |  | 0
202 | Fabricate, Erect and Construction of Elevated Pressed Steel tank, 25cub.m on 9m Tower complete with, Steel tower Columns,Top & Bottom Bearers, Angle bracings,Walkway Platform, handrail,Safety guage, Ladder, Bolts, Nuts, washers and associated Inlet, Outlet, Overflow Drain Pipe and Gate valves | No |  | 1 | 0
| Power House |  |  |  | 0
204 | Design and Construction of new power House with dimension of 10m x 8m | LS |  | 1 | 0
0
| Fencing - Blockwall Perimeter fenc 15m x 20m x 2.7m high |  |  |  | 0 | 750k
237 | Provide and erect barb wire perimeter fence | m2 |  | 189 | 0
Sub-Total Page to Treatment Plant Summary |  |  |  |  | 0
| Gate - Welded steel open grid structure, 3.6m wide X2.1m high, double leaf |  |  |  | 0
238 | Provide and fix welded steel gate 3.6m wide X 2.1m high, in 50mm dia galvanized steel pipe frame and 50mm X 50mm welded galvanized mesh (8 SWG), as in drawing and include for fxing to concrete support posts. Include locking latches and bolts | No |  | 1 | 0
239 | Provide and fix reinforced concrete(C25/20) gate posts 250mm X 250mm X 3.0m long, including Y12 bars, formwork and all ancillaries | LS |  | 1 | 0
240 | Provide and place mass concrete bases (C25/20) to gate posts, 750mm X 750mm X 900mm, including excavation, preparations and backfilling | LS |  | 1 | 0
0
| Landscaping |  |  |  | 0
241 | Allow for land scaping, including grasssing, gravel and kerbstone walkway or others as may be directed on site (Provisional Sum) | PS |  | 1 | 0
242 | Provide and lay kerbstone 400m deep X 200mm wide precast sections in C20/20 concrete. Include for excavations, shoring with 1:4:8 concrete and all ancillary works | m |  | 50 | 0
243 | Provide and lay granite chippings, 900 wide x 100mm thick between kerbstones for accesses | m3 |  | 3 | 0
244 | Grassing to designated areas as may be directed on site, including all surface preparation and imported humus material | m2 |  | 150 | 0
Sub-Total Page to Treatment Plant Summary |  |  |  |  | 0
BILL COLLECTION SHEET
Summary Treatment Plant
| Sheet 1 |  |  |  | 0
| Sheet 2 |  |  |  | 0
Total Treatment Plant |  |  |  |  | 0
Power Supply
Electrical Installations
246 | Provide and instal Manual Change over switch, 150 A | No |  | 1 | 0
247 | Provide and install distribution panel, including relays, contactors, breakers and all cabling for complete electrical operation of the scheme | No |  | 1 | 0
248 | Small power and lighting installations, including wiring | Ls |  | 1 | 0
0
| Connection to National Grid |  |  |  | 0
249 | Supply and install complete overhead line, 50m span, including reinforced concrete poles, cross arms, 11 kV lightining arrestor, disc insulators, 150 mm2 aluminium conductorsarrestor, disc insulators, 150 mm2 aluminium conductors all according to PHCN standards(2 span) all according to PHCN standards | Ls |  | 1 | 0
250 | Earthing of the headworks | Ls |  | 1 | 0
0
Total Power Supply |  |  |  |  | 0
Distribution Network
Clearing work
252 | Removal of stumps, dia: n.e. 1000m., locally disposed | LS |  | 1 | 0
253 | Clearance of wayleaves, pipe dia. n.e. 160mm | m |  | 200 | 0
Pipes and Fitting
Provide and lay uPVC Pipes, plain ened with separate joints or socket & spigot, PN 10 bars
254 | 50mm dia | m |  | 20 | 0
255 | 75mm dia | m |  | 21 | 0
256 | 110 mm dia. | m |  | 20 | 0
0
| Provide and lay fittings in uPVC, PN 10 bars |  |  |  | 0
| Double Socket bends, long radius (LRB) |  |  |  | 0
257 | 50mm dia. PN 10, 11.25o - 90o | No |  | 2 | 0
258 | 75mm dia. PN 10, 11.25o - 90o | No |  | 1 | 0
259 | 110mm dia. PN 10, 11.25o - 90o | No |  | 1 | 0
0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
| Flexible, stepped couplings as stated NP 10 |  |  |  | 0
260 | 75mm uPVC / 80mm ST | No |  | 2 | 0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
| Excavation and Backfilling |  |  |  | 0
| Excavation and Backfilling, including bedding, compaction, |  |  |  | 0
261 | Pipe dia n.e 50mm, max. depth 1 - 1.5m | m3 |  | 9 | 0
262 | Pipe dia n.e 75mm, max. depth 1 - 1.5m | m3 |  | 9.45 | 0
263 | Pipe dia n.e 110mm, max. depth 1 - 1.5m | m3 |  | 9 | 0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
269 | Concrete Stools & Thrustblocks, concrete grade 20/20 to horizontal bends, Junctions, Tapers and Valve stools | Ls |  | 1 | 0
| Service Connections |  |  |  | 0
270 | Water standpipewithin and outside the school premises, including concrete base and taphead with two outlets, as shown in drawings | No |  | 10 | 0
0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
BILL COLLECTION SHEET
Summary Distribution Network
| Sheet 1 |  |  |  | 0
| Sheet 2 |  |  |  | 0
| Sheet 4 |  |  |  | 0
| Sheet 5 |  |  |  | 0
Total Distribution Network to Bill 02_Government Primary and Secondary School Sangassumi (GANYE LGA) Summary |  |  |  |  | 0
BILL | Bill 03_GRA Government Primary and Secondary School Sangassumi (GANYE LGA) |  |  | AMOUNT (NGN)
2 | Borehole |  |  |  | 0
3 | Treatment Works |  |  |  | 0
4 | Power Supply |  |  |  | 0
5 | Distribution Network |  |  |  | 0
TOTAL BILL 02 SUMMARY CARRIED FORWARD TO GANYE SUMMARY |  |  |  |  | 0