## Bill 01_Ganye_Gangaraso WS
ADAMAWA STATE
Small Towns Water Supply
| GANGARASO WATER SCHEME (GANYE LGA) |  |  |  | Bill 01
Item No | Description | Unit | Unit Price (Naira) | Estimated Qty | Amount
(Naira)
100 | General Items
101 | Provide and maintain Project Sign- boards, 2 No per location as directed on site | No |  | 1 | 0
0
102 | Test running of plants for 4 weeks after substantial completion, including running, trouble shooting and performance tests, as specified | Ls |  | 1 | 0
0
103 | Provide stack yard for pipes and appurtenances at suitable location in project area | Ls |  | 1 | 0
0
104 | Provision of As-Built Drawings | Ls |  | 1 | 0
0
105 | Provision of O & M Manuals | Ls |  | 1 | 0
0
106 | Progress photographs/video, as specified | Ls |  | 1 | 0
0
107 | Soil tests for foundation of structures as specified | Ls |  | 1 | 0
0
108 | Structural Design of foundation for elevated tank | Ls |  | 1 | 0
0
109 | Provision for social & economic impact management | Ps |  | 1 | 0
Total General Items to Bill 02 Gangaraso Water Scheme Summary |  |  |  |  | 0
200 | Boreholes
New Boreholes: 4 No.
Mobilization and demobilization
201 | Mobilization and Demobilization of Men, Drilling Rig, Self Loader and all Borehole Drillling Equipment and Materials - Include for site clearing and preparation. | Ls |  | 1 | 0
| Predrilling hydrogeological investigation |  |  |  | 0
202 | Carry out predrilling hydrogeological investigation as specified (with confrimation report submitted) | No |  | 4 | 0
0
| Drilling |  |  |  | 0
203 | Drilling to a required diameter hole of 150mm, in sedimentary formation for installation of 125 mm high presuure (10bar) UPVC casing and screens, depth 0 - 100 m (maximum depth 100m for all locations) | m |  | 400 | 0
204 | Supply and install 125mm 10 bar UPVC casing | m |  | 4 | 0
205 | Supply and install 125 mm upvc screen of 10bar pressure rating (10m maximum length for all locations) | m |  | 4 | 0
206 | Supply and install UPVC adaptor between casing and screen | No |  | 4 | 0
207 | Carry out geophysical (resistivity) logging of the open hole before casing installation | No |  | 4 | 0
208 | Supply and install 2 - 4mm gravel pack as specified in accordance to DIN 4924 Gravel of 1.0 - 2.0 mm (clay-seal top of the gravel pack) | No |  | 4 | 0
209 | Clay seal above gravel pack, 6m depth | No |  | 4 | 0
210 | Backfill drilled material in the annular space on the top of the clay sealing. | No |  | 4 | 0
211 | Grouting and blinding of seal above backfill area, 15m depth and construction of blinding layer 50mm thick around casing in Class 15 concrete. | No |  | 4 | 0
212 | Construction of wellhead slab 250mm thick x 1.2m x 1.2m, in Class 20 concrete, as specified | No |  | 4 | 0
213 | Supply and install protective lockable borehole cap and wellhead nameplate on the casing as specified. Include for making good the area around the casing. | No |  | 4 | 0
Sub-Total Page to Borehole Works Summary |  |  |  |  | 0
Borehole cleaning and test-pumping
214 | Carry out borehole cleaning and development by backwashing, jetting and airlifting | Hr |  | 24 | 0
215 | Equip the borehole with suitable pumpset and ancillary equipment for a 24 pumping test to establish maximum and safe yield from the borehole. Include for measurements and records of discharge water | No |  | 4 | 0
216 | Carry out water quality analysis, including full bacteriological and physico-chemical analysis | No |  | 4 | 0
217 | Carry out disinfection of the motorised borehole, permanent pump and riser pipes as specified | No |  | 4 | 0
218 | Supply and installation of Solar pump type SQ flex +CU200 Type Grundfos or equivalent type/standard) complete with cable, starter/swithces and accessories (provisional). Note: Actual parameters to be determined only from pump-testing result after drilling. | No |  | 4 | 0
219 | Supply and installation of 75 mm dia. UPVC Pipes of 10 bar flanged with all connections to form rising main | m |  | 4 | 0
220 | Supply and Install 3m scotch cast cable jointing kits and earthing | No |  | 4 | 0
221 | Supply and Installation of Solar Mono polycrystalline panels as in TSS (1650 Watts) | Watts |  | 3 | 0
222 | Supply and Install support strucure and frames for panels | No |  | 4 | 0
223 | Supply and Install 3x6mm2 pump motor cable | Set |  | 4 | 0
224 | Supply and Install 4mm2 interconnector cable | Set |  | 4 | 0
225 | Supply and install Marine rope 10mm as antidrop for the pump | Roll |  | 4 | 0
226 | Provide and install header pipework, in 75mm dia upvc pipes, fittings, and appurtenances including 1 no 90 deg and 2 nos 45 deg bends, air valve, gate valve, non-return valve, pressure gauge and flow meter. | No |  | 4 | 0
227 | Carry out 6-hour pump test after installation of permanent pump | Hr |  | 24 | 0
232 | Equip the borehole with suitable pump set and ancillary equipment for pump testing by constant and step and draw down tests. Test pump to establish maximum and safe yield from the borehole. Include for measurements and records of discharge water | No |  | 4 | 0
234 | Carry out water quality analysis, including full bacteriological and physico-chemical analysis | No |  | 4 | 0
235 | Carry out disinfection of borehole as specified | No |  | 4 | 0
236 | Prepare Technical Report (allow 5 copies) for the boreholes test pumping and construction details. Include for borehole material logs, yields, recovery, water quality analysis (full chemical and bacteriological) and borehole vertical alignment including Operation & Maintenance Manuals and drawings | Ls |  | 1 | 0
Sub-Total Page to Borehole Works Summary |  |  |  |  | 0
COLLECTION SHEET
Summary Borehole Works
| Sheet 1 |  |  |  | 0
| Sheet 2 |  |  |  | 0
Total Borehole Works to Bill 02_ Gangaraso Water Scheme Summary |  |  |  |  | 0
300 | Treatment Plant
Treatment is required for pH correction and disinfection only.
Dosing Pumps
301 | Chemical dosing set for each of Soda ash(Sodium Carbonate) and Chlorine (Calcium hypochlorite), including Dosing Pump with pumping rate 50 Litres/Hr and 4 bar working pressure, mixing tank 1000 Litres, level indicator and chemical agitator, 12mm dia uPVC connection pipework and all ancillaries for complete system installation. | LS |  | 1 | 0
0
| Storage Tanks |  |  |  | 0
302 | Fabricate, Erect and Construction of Elevated Pressed Steel tank, 50cub.m on 10m Tower complete with, Steel tower Columns,Top & Bottom Bearers, Angle bracings,Walkway Platform, handrail,Safety guage, Ladder, Bolts, Nuts, washers and associated Inlet, Outlet, Overflow Drain Pipe and Gate valves | No |  | 1 | 0
304 | Construct reinforced concrete foundation, in accordance with results of geophysical investigation | Ps |  | 1 | 0
305 | Rehabiltation of suction tank as ground tank storage for transfer to Elevated Storage Tank | Ps |  | 1 | 0
| Power House |  |  |  | 0
307 | Design and Construction of new power House with dimension of 10m x 10m | LS |  | 1 | 0
0
| Fencing - Blockwall Perimeter fenc 15m x 20m x 2.7m high |  |  |  | 0
308 | Provide and erect barb wire perimeter fence | m2 |  | 180 | 0
Sub-Total Page to Treatment Plant Summary |  |  |  |  | 0
| Gate - Welded steel open grid structure, 3.6m wide X2.1m high, double leaf |  |  |  | 0
309 | Provide and fix welded steel gate 3.6m wide X 2.1m high, in 50mm dia galvanized steel pipe frame and 50mm X 50mm welded galvanized mesh (8 SWG), as in drawing and include for fxing to concrete support posts. Include locking latches and bolts | No |  | 1 | 0
310 | Provide and fix reinforced concrete(C25/20) gate posts 250mm X 250mm X 3.0m long, including Y12 bars, formwork and all ancillaries | LS |  | 1 | 0
311 | Provide and place mass concrete bases (C25/20) to gate posts, 750mm X 750mm X 900mm, including excavation, preparations and backfilling | LS |  | 1 | 0
0
| Landscaping |  |  |  | 0
312 | Allow for land scaping, including grasssing, gravel and kerbstone walkway or others as may be directed on site (Provisional Sum) | PS |  |  | 0
313 | Provide and lay kerbstone 400m deep X 200mm wide precast sections in C20/20 concrete. Include for excavations, shoring with 1:4:8 concrete and all ancillary works | m |  | 50 | 0
314 | Provide and lay granite chippings, 900 wide x 100mm thick between kerbstones for accesses | m3 |  | 3 | 0
315 | Grassing to designated areas as may be directed on site, including all surface preparation and imported humus material | m2 |  | 150 | 0
Sub-Total Page to Treatment Plant Summary |  |  |  |  | 0
BILL COLLECTION SHEET
Summary Treatment Plant
| Sheet 1 |  |  |  | 0
| Sheet 2 |  |  |  | 0
Total Treatment Plant to Bill 02_ Gangaraso Water Scheme Summary |  |  |  |  | 0
Power Supply
Electrical Installations
401 | Provide and instal Manual Change over switch, 150 A | No |  | 1 | 0
402 | Provide and install distribution panel, including relays, contactors, breakers and all cabling for complete electrical operation of the scheme | No |  | 1 | 0
403 | Small power and lighting installations, including wiring | Ls |  | 1 | 0
| Motor Control Panel |  |  |  | 0
404 | 415 volts 50Hz, 3 – phase, 250amps with fusible disconnection switch. Push buttons for start and stop, 1 pumps, 2 Nos dosing pumps, 2 Nos transfer pumps and all internal electrical fittings with all fuses complete. All electrical starters shall consist of terminal overload relay of rating suitable to motor control. Indicator lamp for various equipment and on/off reset button to get mounted on cover to panel | No |  | 1 | 0
0
| Connection to National Grid |  |  |  | 0
405 | Supply and install complete overhead line, 50m span, including reinforced concrete poles, cross arms, 11 kV lightining arrestor, disc insulators, 150 mm2 aluminium conductorsarrestor, disc insulators, 150 mm2 aluminium conductors all according to PHCN standards(2 span) all according to PHCN standards | Ls |  | 1 | 0
406 | Earthing of the headworks | Ls |  | 1 | 0
0
Total Power Supply to Bill 02_Gangaraso Water Scheme Summary |  |  |  |  | 0
500 | Distribution Network
Clearing work
501 | Removal or trees, girth: n.e. 1000m., locally disposed | LS |  | 1 | 0
502 | Removal of stumps, dia: n.e. 1000m., locally disposed | LS |  | 1 | 0
Pipes and Fitting
Provide and lay uPVC Pipes, plain ened with separate joints or socket & spigot, PN 10 bars
503 | 50mm dia | m |  | 4200 | 0
504 | 75mm dia | m |  | 4200 | 0
506 | 110 mm dia. | m |  | 600 | 0
0
| Provide and lay fittings in uPVC, PN 10 bars |  |  |  | 0
| Double Socket bends, long radius (LRB) |  |  |  | 0
507 | 50mm dia. PN10, 11.25o - 90o | No |  | 21 | 0
508 | 75mm dia. PN10, 11.25o - 90o | No |  | 21 | 0
509 | 110mm dia. PN10, 11.25o - 90o | No |  | 3 | 0
0
| Junctions, Double socket c/w plain ended branch |  |  |  | 0
510 | 75/50mm dia. | No |  | 21 | 0
511 | 75/75mm dia. | No |  | 3 | 0
512 | 50/50mm dia. | No |  | 21 | 0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
Tapers, Double socket, concentric,
513 | 50/75mm dia. NP 9 | No |  | 21 | 0
0
| Adaptors and Couplings |  |  |  | 0
| uPVC Flanged adaptor, flexible, NP 10 |  |  |  | 0
513 | To suit 50mm dia. | No |  | 21 | 0
514 | To suit 75mm dia. | No |  | 6 | 0
515 | To suit 90mm dia. | No |  | 6 | 0
0
| End pieces |  |  |  | 0
538 | End cap 50 dia. PN 10 | No |  | 21 | 0
539 | End cap 75 dia. PN 10 | No |  | 6 | 0
541 | End cap 110 dia. PN10 | No |  | 6 | 0
0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
0
| Junctions and branches, for Air valves |  |  |  | 0
543 | 75/50mm dia PN 9/10 | No |  | 6 | 0
0
| DI / ST Flexible, straight couplings as stated, NP 10 |  |  |  | 0
0
| End pieces |  |  |  | 0
544 | Blank flange 75mm dia. PN 9/10 | No |  | 6 | 0
0
| Gate Valves |  |  |  | 0
| Provide and instal flanged, non-rising spindle type with cap & key, PN 10 |  |  |  | 0
545 | 50mm - 75mm dia. | No |  | 4 | 0
546 | 90mm dia. | No |  |  | 0
547 | 110mm dia. | No |  | 2 | 0
0
| Provide and instal flanged, non-rising spindle type with extension spindle & cap & key, PN 10, to Fire Hydrant isolators & W.Os |  |  |  | 0
573 | 65mm dia. | No |  | 4 | 0
574 | 75mm dia. | No |  | 3 | 0
0
| Flap Valves, flanged, to WOs (provide and install) |  |  |  | 0
575 | 50mm dia. PN 10 | No |  | 2 | 0
576 | 75-110mm dia. PN 10 | No |  | 1 | 0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
Air valves,
Provide and install flanged Air Valves, anti-shock, antisurge type, complete with fittings as shown in drawings
577 | 50 -110mm dia, PN 9/10 | No |  | 3 | 0
0
0
| Excavation and Backfilling |  |  |  | 0
| Excavation and Backfilling, including bedding, compaction, |  |  |  | 0
578 | Pipe dia n.e 50mm, max. depth 1 - 1.5m | m3 |  | 1890 | 0
579 | Pipe dia n.e 75mm, max. depth 1 - 1.5m | m3 |  | 1890 | 0
580 | Pipe dia n.e 110mm, max. depth 1 - 1.5m | m3 |  | 270 | 0
0
| Flushing, Disinfection and Pressure Testing |  |  |  | 0
581 | Flushing and disinfection of new pipelines | m |  | 4 | 0
582 | Pressure testing of pipeline | m |  | 4 | 0
0
| Concrete Chambers and Ancillaries |  |  |  | 0
0
| Valve Chambers |  |  |  | 0
583 | Blockwork gate valve chamber ,clear opening 750mm X 750mm, in 225mm blockwork filled solid in C10/20 concrete, depth n.e. 1.5 m. Include for lockable precast cover slabs in 950mm x 250mm x 100mm thick sections | No |  | 4 | 0
584 | Masonry or blockwork air valve chamber ,clear opening 750mm X 750mm, in 225mm blockwork filled solid in C10/20 concrete, depth n.e. 1.5 m. Include for lockable precast cover slabs in 950mm x 250mm x 100mm thick sections | No |  | 4 | 0
585 | Concrete outfall chamber for WOs, in C20/20 concrete, as shown in drawings | No |  | 4 | 0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
Reinstatement of Roads
586 | Breaking up, temporary and permanent reinstatement of tarmac roads as specified, width n.e., 900mm | m |  | 20 | 0
587 | Breaking up, temporary and permanent reinstatement of unpaved roads as specified, width n.e. 900mm | m |  | 25 | 0
0
| Marker Posts |  |  |  | 0
588 | Marker Posts for Sluice valves, Air valves, Fire hydrants , Washouts, Meters | No |  | 12 | 0
| Service Connections |  |  |  | 0
0
589 | Water standpipe no., including concrete base and taphead with two outlets, as shown in drawings | No |  | 10 | 0
0
Sub-Total Page to Distribution Network Summary |  |  |  |  | 0
BILL COLLECTION SHEET
Summary Distribution Network
| Sheet 1 |  |  |  | 0
| Sheet 2 |  |  |  | 0
| Sheet 3 |  |  |  | 0
| Sheet 4 |  |  |  | 0
| Sheet 5 |  |  |  | 0
Total Distribution Network to Bill 02_ Gangaraso Water Scheme Summary |  |  |  |  | 0
BILL | Bill 01_Gangaraso Water Scheme Summary |  |  | AMOUNT (NGN)
1 | Preliminary and General |  |  |  | 0
2 | Borehole |  |  |  | 0
3 | Treatment Works |  |  |  | 0
4 | Power Supply |  |  |  | 0
5 | Distribution Network |  |  |  | 0
TOTAL BILL 02 SUMMARY CARRIED FORWARD TO GRAND SUMMARY |  |  |  |  | 0